HQE Energy compliance report

Richard Quincey

Rev A

30/06/2026

Contents

1

Contents	2

Summary	3

RE2020 – All	4

The 3 Core Pillars of RE2020	4

RE2020 – Energy	4

Energy performance	4

Certification	5

Title V process	6

Standards	6

Use of alternative engines	7

VE product	7

RE2020 Comfort	8

Method	8

VE Product	9

RE2020 Daylight	10

Method	10

Simulated approach	10

VE Product	10

RE2020 Clear view	11

Method mandatory minimum	11

Method advanced	11

VE product	12

Actions	13

Summary

This is a review of the potential of using the VE for French HQE (2020) compliance purposes. The VE could potentially address HQE credits:

- Energy – significant consumption increment on RT 2012, fabric first & local renewables.

- Summer comfort – comfort without excessive air-conditioning.

- Daylighting – sDA.

- View outside – ray-traced line of sight.

RE 2020 mandates the use of “Th-BCE 2020" algorithm (engine) developed by the CSTB for energy & comfort compliance. Thus, this report looks at all of the above credits as part of strengthening a user proposition for selling the VE in this market.

Only certified commercial interfaces that natively run the Th-BCE engine (such as ClimaWin, Pleiades, Perrenoud, or Visual TTH) can generate the legal compliance certificate (attestation RE2020) needed for planning permission.

IESVE could be supplied with the datasets (occupancy, weather etc) for users to faciliate design then export to a RE2020 tool for regulatory compliance.

There is a process (Title V) used to bypass the rigid constraints of the national Th-BCE 2020 engine, however this does not look practical on a typical project basis.

RE2020 evaluates comfort by calculating cumulative heat discomfort over an entire year, forcing designers to optimize building envelopes against worsening heatwaves without defaulting to mechanical air conditioning. The assessment mandates the "Th-BCE 2020" algorithm (engine).

If a design cannot meet the rigid 1/6th glazing requirement, RE2020 permits a dynamic daylight simulation (Autonomie Lumineuse) as a regulatory alternative, so there is potential here.

RE2020 introduces a qualitative daylight check alongside numerical lux targets. For residential buildings, an occupant standing at least 1 metre away from the interior facade in at least one primary living space must have a completely uninhibited, direct visual line of sight to the outdoor environment, so there is potential here.

To deliver a viable product we would need to consider:

- If integrating RE2020 model data in the VE offers an attractive proposition for parallel design energy iteration.

- Whether a design RE2020 comfort tool in the VE offers an attractive proposition

- Users accept / use the current DA & sDA tools.

- If a new clear view tool (also UK BR209) has value.

- Tool & reportage language.

The following sections are technical investigations using Gemini (public) without context uploads.

RE2020 – All

RE2020 is France's stringent environmental code for new construction. It mandates that new buildings lower energy consumption, reduce their carbon footprint across their entire life cycle, and withstand extreme summer heatwaves without air conditioning.

The 3 Core Pillars of RE2020

- Energy Performance: Drastically reduces consumption limits compared to older standards (e.g., maximum primary energy consumption generally under 100 kWh/m² per year).

- Life Cycle Carbon Impact: Enforces Dynamic Life Cycle Analysis (LCA) to cap greenhouse gas emissions from both construction materials and the demolition phase.

- Summer Comfort: Requires buildings to maintain comfortable indoor temperatures during heatwaves, measured using degree-hours (DH) without relying on excessive air conditioning.

RE2020 – Energy

Energy performance

The Energy Performance element of France's RE2020 regulatory framework is structured entirely around driving building envelopes to a "fabric-first" standard and shifting energy systems toward local renewables.

Rather than prescribing specific equipment or insulation values, it sets strict, outcome-based performance targets evaluated via national calculation standards.

To achieve energy compliance, a building must simultaneously pass three primary regulatory ceilings (known as coefficients max).

- Bbio (Fabric Demand)  ≤ Bbio_max (Points)

The intrinsic heating, cooling, and artificial lighting demand of the building envelope, completely independent of the actual HVAC equipment chosen.

Must be less than Bbio_max. RE2020 drops this ceiling by roughly 30% compared to the older RT2012 code.

Typically, around 63 points for a single-family home in central France (Zone H1), though it adjusts dynamically.

- Cep (Total Primary)  ≤ Cep_max (kWh_ep/m²/yr)

The total primary energy consumed by the building annually. RE2020 expands this to cover 5 standard items (heating, cooling, domestic hot water, lighting, ventilation) plus auxiliary loads (e.g., parking lot lighting, escalators).

Must be less than Cep_max. Generally targeted to sit under 100 kWh_ep/m²/year.

3. Cep,nr (Non-Ren.)    ≤ Cep,nr_max (kWh_ep/m²/yr)

The fraction of the total energy consumption (Cep) derived purely from non-renewable or fossil fuel sources.

Must be less than Cep,nr_max. This targets a steep reduction (e.g., max 55 kWh_ep/m²/year in Zone H1), effectively banning standard natural gas boilers from new residential projects.

While outcomes are flexible, RE2020 retains several strict baseline building rules:

- Glazing Ratio: Glazed surfaces must account for at least 1/6th of the total livable floor area to maximize natural daylighting.

- Airtightness: Enforces systematic pressure testing at completion. Residential units must achieve an air leakage metric (\(Q_{4Pa\_surf}\)) below 0.60 m³/(h.m²) for houses and 1.00 m³/(h.m²) for multi-family blocks.

- Thermal Bridging: The global thermal bridge coefficient (Ψ₉) cannot exceed 0.28 W/(m².K).

Certification

Compliance requires specific software certified by the French government.

- The Regulatory Engine: Calculations must use the official, national "Th-BCE 2020" algorithm developed by the CSTB (Centre Scientifique et Technique du Bâtiment).

- Climate Modulation: Raw targets are adjusted dynamically per project according to geographic climate zones (H1a to H3, ranging from cold northern zones to the warm Mediterranean coast), altitude, surface area, and whether noise pollution forces windows to stay closed.

The "Fictional" Cooling Penalty: If a design lacks active air conditioning but scores highly on the Summer Comfort metric (above 350 Degree-Hours), the methodology automatically injects a virtual energy penalty into the Cep calculation. This forces the software to assume occupants will eventually buy portable AC units due to poor design.

The core philosophical difference explains why generic simulation engines are rejected for compliance:

- RE2020 (Th-BCE) is an Accountability Tool: It enforces standardized, non-negotiable occupant behavior profiles, fixed internal heat gains, mandatory weather data sets with specific heatwave sequences, and strict French carbon accounting rules.

EnergyPlus / IESVE Apache are Design Tools: These engines utilize Dynamic Thermal Simulation (STD—Simulation Thermique Dynamique) based on real-world, customizable schedules and physics. Because they allow the user to modify occupancy schedules or ventilation control strings freely, they cannot guarantee a standardized "apples-to-apples" compliance review across different real estate project.

Title V process

The Title V (Titre V) process is the official regulatory mechanism used to bypass the rigid constraints of the national Th-BCE 2020 engine. Managed under French law by the CSTB, it allows manufacturers, designers, or network operators to scientifically prove the energy or carbon performance of an innovation so it can be legally factored into RE2020 compliance certificates.

There are three distinct types of Title V applications, each requiring a specific approach to get approved.

Before applying via the Ministry of Ecological Transition Title V Portal, you must select one of three administrative routes:

- Titre V Opération (Project-Specific): Used by a design team for a single, specific construction project. You demonstrate how an unusual design or localized system achieves RE2020 goals despite not fitting into the commercial software inputs. [1]

- Titre V Système (System/Product): Usually driven by HVAC or material manufacturers. Once approved, the CSTB writes a specific calculation method for that product into law, forcing commercial RE2020 software developers to add it as a standard entry drop-down.

Titre V Réseau (District Networks): Used by district heating and cooling network operators to register a new or heavily greened energy grid. This assigns provisional carbon and energy performance metrics to the network so nearby new buildings can claim the carbon benefits immediately.

The process is effectively running a simulation alongside "Th-BCE 2020" to generate an adjustement.

The problem for projects is that the Titre V Opération takes at least 3 to 6 months to process, while a Titre V Système can take over a year. This is not practical for typical projects.

Standards

The entire RE2020 framework is constructed on French structural law while aligning directly with broader European energy rules:

- French Decree No. 2021-1004 & Order (Arrêté) of August 4, 2021: These are the primary legal texts that anchor the energy performance goals, indicators, and thresholds into French law.

- NF EN ISO 52000-1: The foundational standard used by the engine for calculating overarching building energy performance and defining primary energy factors.

- NF EN ISO 13789 / GA P50-784: Governs the calculation methodologies for transmission and ventilation heat transfer coefficients.

- EU Energy Performance of Buildings Directive (EPBD): RE2020 serves as France’s mechanism to fulfill the EU's updated EPBD mandates, forcing the rollout of Zero-Emission Buildings (ZEB) via strict decarbonization timelines.

Use of alternative engines

Alternative calculation engines like EnergyPlus or IESVE Apache cannot be used directly to prove legal compliance with RE2020.

To legally validate a building in France, you must use software explicitly approved by the French government. This software must embed the exact, unmodified national "Th-BCE 2020" core algorithm developed by the CSTB (Centre Scientifique et Technique du Bâtiment).

While these engines cannot be used for the legal paperwork, they are frequently used alongside the Th-BCE engine on complex, high-performance projects:

- Phase 1: Optimization (IESVE / EnergyPlus): Engineers use these engines during early design to size HVAC systems, run micro-climate shading analysis, and closely study "Summer Comfort" thermodynamics using high-resolution, sub-hourly physics.

- Phase 2: Translation: The resulting building geometry, insulation values, and system capacities are then manually entered into a certified French RE2020 tool.

- Phase 3: Legal Sign-off (Th-BCE 2020): The certified tool calculates the official Bbio, Cep, and Cep,nr points using the rigid regulatory algorithm to produce the building permit documentation.

VE product

So "Th-BCE 2020" is locked down and looks similar to an SBEM situation.

The VE can be used for design iteration and then we export to a certified tool; do we partner of leave this to the user?

To improve UX we could offer:

RE2020 Navigator.

A RE2020 dataset: fixed internal heat gains, profiles, mandatory weather data sets with specific heatwave sequences etc.

Output: French carbon accounting rules, regional carbon factors etc.

Reporting: to suit the needs of RE2020 users.

RE2020 Comfort

Provide details of the targets and methodology (including referenced standards) required for the Summer Comfort element of RE 2020?

Method

The Summer Comfort (Confort d’Été) element of RE2020 introduces a radical shift in how passive cooling performance is legally evaluated in France.

Rather than relying on peak summer temperatures, RE2020 evaluates comfort by calculating cumulative heat discomfort over an entire year, forcing designers to optimize building envelopes against worsening heatwaves without defaulting to mechanical air conditioning.

1. Core Target: The Degree-Hours (DH) Indicator

The metric used to determine compliance is the Degree-Hours (DH) indicator. This index quantifies both the duration and intensity of indoor overheating during the warmest months.

The Discomfort Thresholds

The regulatory calculation engine assumes indoor discomfort begins when the indoor temperature crosses a dynamic threshold (\(T_{limit}\)), which ranges from 26°C to 28°C.

- The Lower Limit (26°C): Enforced during the night (from 10:00 PM to 7:00 AM) to ensure occupants can sleep comfortably.

- The Dynamic Day Limit (26°C to 28°C): Changes based on the outdoor ambient temperature of the preceding days. If the preceding days were exceptionally hot, the human body adapts, and the indoor limit rises up to 28°C.

- For every hour the internal temperature delta is recorded. The annual sum determines the final score. Every project must pass through a two-tiered threshold system to assess compliance:

  - DH < 350 DH       -->  FULLY COMPLIANT        (No Penalties, Comfort Assured)

  - 350 ≤ DH ≤ DH_max -->  CONDITIONALLY COMPLIANT   (Virtual Energy Penalty Added)

  - DH > DH_max       -->  NON-COMPLIANT    (Building Permit Rejected)

- To accurately calculate the DH value, the standardized calculation methodology uses the national "Th-BCE 2020" algorithm, applying specific evaluation parameters:

- Spatially Averaged Zones: The calculation evaluates the building by distinct thermal zones (e.g., separating day zones like living rooms from night zones like bedrooms).

- Mandatory Climatological Sequences: The engine uses updated climate files representing recent historical baselines. Crucially, it injects an explicit fictional 8-day extreme heatwave sequence matching severe contemporary weather anomalies.

- Standardized Blind and Shutter Control: Designers cannot assume occupants will perfectly manage blinds. The engine overrides manual profiles, forcing standardized, automation-dependent operational schedules for external solar protections based on incoming solar irradiance.

- Night Ventilation Modelling: The engine factors in the potential cooling benefit of night ventilation, but scales down its effectiveness if the project is located in a high-crime or high-noise zone where windows cannot safely remain open overnight.

The scientific, meteorological, and mathematical architecture underpinning the Summer Comfort calculations relies on several key frameworks:

- French Decree No. 2021-1004 & Order of August 4, 2021: The core statutory legal frameworks establishing the DH indicators, adaptive temperature baselines, and legal limits.

- NF EN ISO 52016-1: The primary international standard utilized by the engine to simulate dynamic hourly energy balances, sensible heating/cooling loads, and internal indoor temperatures.

- NF EN 16798-1: Governs indoor environmental input parameters, specifically framing the adaptive thermal comfort models used to dictate the dynamic \(T_{limit}\) scaling between 26°C and 28°C.

- CSTB Th-BCE 2020 Rules Document: The official technical book detailing the precise algorithmic implementation of the thermal inertia matrix and solar shading calculations.

VE Product

So "Th-BCE 2020" comfort is locked down like for energy.

The VE could be used for design iteration and then we export to a certified tool, but implementing the method used for comfort would be a significant EPIC in its right.

Defining zones, specific climate files (are they available?), blind control profiles, night ventilation controls (profiles) plus the post-processing the DH indicator would be required.

RE2020 Daylight

Provide details of the targets and methodology (including referenced standards) required for the daylighting element of RE 2020?

Method

Daylight assessment is a formal part of RE2020. It is integrated through both mandatory prescriptive targets and advanced spatial daylight autonomy simulations.

Rather than treating lighting purely as an electrical drain, RE2020 frames natural daylight as a critical health, well-being, and passive energy asset.

The baseline daylight requirement for residential projects is a prescriptive geometry check. The total surface area of transparent windows and glazed doors must equal at least 1/6th (16.7%) of the total liveable floor area (Surface de Référence).

If a design cannot meet the rigid 1/6th architectural layout (e.g., due to dense urban constraints or structural restrictions), RE2020 permits a dynamic daylight simulation (Autonomie Lumineuse) as a regulatory alternative.

Simulated approach

To bypass the 1/6th rule and achieve compliance, an engine must prove the project achieves two simultaneous illuminance targets across the home's living areas:

- The 300 Lux Target: At least 50% of the living space area must reach a minimum illuminance of 300 lux for more than half of all daylight hours throughout the year.

The 100 Lux Target: At least 95% of the living space area must reach a minimum illuminance of 100 lux for more than half of all daylight hours throughout the year.

It is unclear if blinds are involved in this assessment (i.e. is it DA or sDA to LM83).

VE Product

The DA or sDA method look like it is likely provided for already in RadianceIES, the user just needs to set the dual post-processing targets.

RE2020 Clear view

Provide details of the method required for the clear view element of RE 2020?

RE2020 introduces a qualitative daylight check alongside numerical lux targets. For residential buildings, an occupant standing at least 1 metre away from the interior facade in at least one primary living space must have a completely uninhibited, direct visual line of sight to the outdoor environment.

Method mandatory minimum

The absolute fundamental requirement dictates that the total surface area of all openings (windows, glass doors, etc.) must be at least 1/6th (or approximately 16.7%) of the total habitable surface area.

How you measure the elements matters strictly in the RE 2020 calculations:

- The Window Area: The openings are measured via cote tableau (rough opening/structural masonry frame size). This includes both the transparent glazing area (clair de vitre) and the surrounding structural woodwork/frame (dormant and ouvrant).

- The Entrance Door: Main entrance doors are fully counted toward the total window opening area, regardless of whether they are solid or glazed.

Habitable Surface Area: Calculated by taking the interior floor area with a ceiling height of at least 1.80m. It includes primary living spaces, corridors, bathrooms, and integrated laundries, but strictly excludes unheated extensions, garages, basements, or balconies.

While the 1/6th rule is a baseline requirement, RE 2020 assesses the precise properties of the glass element through software calculations defined under the Th-Bat 2020 rules. These look directly at the actual clear view performance:

- Light Transmission: The percentage of natural light allowed through the clear portion of the glass, impacting the building's Bbio (Bioclimatic need) indicator.

Solar Factor (g or Sw): The percentage of direct solar energy transmitted into the room to leverage passive heating in the winter while ensuring summer thermal comfort through solar protection elements.

Method advanced

For the clear view to the outside is a raytraced method applicable?

Yes, a ray-traced method is applicable, but its exact usage depends entirely on whether you are satisfying the mandatory regulatory minimums or conducting a more advanced visual comfort simulation.

Under France's RE 2020 framework, the application of ray tracing is broken down into two distinct categories:

1. In Regulatory RE 2020 Software (Direct Calculation)

For standard regulatory compliance (generating your official RSET/RSEE files), you cannot use a custom standalone ray tracer to override the baseline calculation.

- The Core Calculation: The official RE 2020 core calculation engine (Th-BCE 2020) relies on deterministic, simplified geometric algorithms to calculate solar masks and window properties.

- Ray-Tracing Integration: Certain CSTB-certified RE 2020 software suites—most notably ArchiWIZARD—actively embed real-time 3D ray-tracing engines into their BIM model interfaces. In this context, ray tracing is used internally by the software to automatically calculate exact solar trajectories, cast complex geometric shadows from surrounding buildings, and accurately measure daylight coefficients inside rooms, which are then passed into the regulatory compliance engine.

2. In Advanced Dynamic Simulations (Daylighting & Visual Comfort)

If your building project is aiming for advanced environmental labels, tertiary workspace compliance, or strict summer comfort metrics via Dynamic Thermal Simulation (STD), physically-accurate ray tracing is the industry standard.

- Daylight Factor (FLJ - Facteur Lumière Jour): For non-residential buildings, or high-end residential projects targeting strict visual comfort, ray-tracing programs are used to calculate the FLJ. This measures the percentage of outdoor natural light reaching the interior under a completely overcast sky.

- Standard Tools: Architects and thermal engineers routinely use ray-tracing software like Radiance (often driven via Ladybug Tools in Grasshopper/Rhino) to execute Monte Carlo light-backscattering simulations. This determines if the outside view and indoor glare are adequately optimized.

You cannot use ray tracing to bypass the basic geometric "1/6th rule" surface calculation. However, you can and should use ray tracing via certified software to accurately calculate how much of that "clear view" actually translates into real solar gains (Bbio) and summer thermal comfort (DH - Degrés-Heures) without creating problematic glare

VE product

So, it appears that we can use RadianceIES for assessing clear view. It looks similar to BR209 2022 view out. This feature has not yet been implemented but is specified in incubation here Feature 51787.

Actions

Concentrate on energy piece only at this stage given resource window

Do we have a user(s) who can validate the tool design / help with queries?

Agree Title V process is not usable

Finalise language aspects (English only or French Navigator / report option?)

Clarify any copyright & chargeable aspects (e.g. weather)

Define user model workflow

Clarify simple HVAC rather than ApHVAC is required

Investigate weather format /compatibility with VE (heat-wave sequences)

Clarify – are we incorporating “Th-BCE 2020" algorithm (engine) developed by CSTB in the VE (like SBEM) or are we outputting a file for input into a third party certified commercial interfaces that natively run the Th-BCE engine (such as ClimaWin, Pleiades, Perrenoud, or Visual TTH)?

Understand “Th-BCE 2020" accounting regulations – how far are we going producing “Th-BCE 2020" results in the VE for users in the design stage?

Get “Th-BCE 2020" climate data

Get “Th-BCE 2020" primary energy factors

Get “Th-BCE 2020" CO₂ conversion factors

Does “Th-BCE 2020" use actual / reference models or is it an absolute actual model only?

Summer comfort seems integral to the energy target (virtual cooling energy penalty into the Cep calculation)

Get “Th-BCE 2020" climate-based target adjustments (H1a to H3)

Define model datasets:

  - Weather (& locations list)

  - Building types

  - Space templates

  - Profiles

  - Constructions (roofs, walls, floors, glazing, rooflights, doors)

    - Thermal bridging (looks like Psi values, take-off dim method?)

    - Air tightness (implementation method?)

  - Systems (heating, cooling, DHW, CoP etc)

  - Lighting

  - Power / plug loads

  - Auxiliary energy

  - PVs

  - CHP

  - Escalators

  - Exterior lighting

  - etc

Determine model building rules from design model:

  - Zoning (comfort)

  - Blind controls (comfort)

  - Night ventilation (comfort)

  - User editing limitations

Resolve Output mapping

  - Metering

Determine Navigator tree from workflow

Understand definition of floor area

Get sample reportage / draft mock-up